{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":140,"n_cols":5,"rows_kept":140,"merged":[[1,0,1,4],[42,0,42,4],[43,0,43,4],[59,0,59,4],[61,0,61,4],[118,0,118,4],[119,0,119,4],[133,0,133,4],[134,0,134,4]],"flags":["formulas_cached_only"]}
[]
["Function Code 03 - Read holding Registers(Single_Phase_UPS)"]
[]
["Register","Query Address","Size","Measurement","Notes"]
[{"$nulls":3}," UPS  Information Group"]
["40001 - 40007","0000 - 0006","14 characters","UPS Company Name","14 characters"]
["40008 - 40012","0007 - 0011","10 characters","UPS Model","10 characters"]
["40013 - 40017","0012 - 0016","10 characters","version number of the UPS firmware","10 characters"]
["40018 - 40025","0017 - 0024","16 characters","firmware revision of the UPS SNMP Proxy agent.","16 characters"]
[{"$nulls":3},"Battery Group"]
[40026,"0025","UWORD","Battery Status","Integer Value: unknown(1),batteryNormal(2),batteryLow(3)"]
[40027,"0026","UWORD","Seconds on Battery","Seconds"]
[40028,"0027","UWORD","Battery Capacity","0-100%"]
[40029,"0028","UWORD","Battery Voltage","x0.01 VA"]
[40030,"0029","UWORD","Battery Temperature","x0.1 ℃"]
[40031,"0030","UWORD","Battery Current","x0.1 A"]
[40032,"0031","UWORD","Total Battery Voltage","x0.01 VA"]
[{"$nulls":3}," Input Group"]
[40040,"0039","UWORD","Input Line Voltage","x0.1 VAC"]
[40041,"0040","UWORD","Input Max Line Voltage","x0.1 VAC"]
[40042,"0041","UWORD","Input Min Line Voltage","x0.1 VAC"]
[40043,"0042","UWORD","Input Frequency","x0.1 Hz"]
[40044,"0043","UWORD","Input Current","x0.1 A"]
[40045,"0044","UWORD","Input True Power","Watts"]
[{"$nulls":3},"Output Group"]
[40050,"0049","UWORD","Output Status","Integer Value:unknown(1),onLine(2),onBattery(3),onBoost(4),sleeping(5),onBypass(6),rebooting(7),standBy(8),onBuck(9)"]
[40051,"0050","UWORD","Output Voltage","x0.1 VAC"]
[40052,"0051","UWORD","Output Frequency","x0.1 Hz"]
[40053,"0052","UWORD","Output Load","0-100%"]
[40054,"0053","UWORD","Output Current","x0.1 A"]
[40055,"0054","UWORD","Output True Power","Watts"]
[null,null,"UWORD","Rating Group"]
[40060,"0059","UWORD","Rating Voltage","x0.1 VAC"]
[40061,"0060","UWORD","Rating Power","VA"]
[40062,"0061","UWORD","Rating Battery Voltage","x0.01 VA"]
[40063,"0062","UWORD","Rating Frequency","x0.1 Hz"]
[{"$nulls":3},"Alarm Group"]
[40064,"0063","UWORD","Utility Fail","Integer Value: Yes(1),No(2)"]
[40065,"0064","UWORD","UPS Failed","Integer Value: Yes(1),No(2)"]
[40066,"0065","UWORD","Test in Progress","Integer Value: Yes(1),No(2)"]
[40067,"0066","UWORD","Shutdown Active","Integer Value: Yes(1),No(2)"]
[40068,"0067","UWORD","Beeper On ","Integer Value: Yes(1),No(2)"]
["Function Code 06 - Write Single Register"]
["Function Code 16 - Write Multiple Registers"]
[]
[{"$nulls":3},"Config Group"]
[40070,"0069","UWORD","Config ups Shut off Delay","The delay in seconds the UPS remains on after being told\nto turn off.  Allowed values are 12, 18, 24, 30, 36, 42,\n48, 54, 60, 120, 180, 240, 300, 360, 420, 480, 540, and\n600 seconds."]
[40071,"070","UWORD","Config Ups Sleep Time","Integer Value: 1 - 9999"]
[{"$nulls":3},"Control Group"]
[40080,"0079","UWORD","Control UPS Off","Integer Value: turnUpsOff(2)"]
[40081,"0080","UWORD","Control Reboot Ups","Integer Value: rebootUps(2)"]
[40082,"0081","UWORD","Control UPS Sleep","Integer Value: noPutUpsToSleep(1),putUpsToSleep(2)"]
[40083,"0082","UWORD","Control Simulate Power Fail","Integer Value: simulatePowerFailure(2)"]
[40084,"0083","UWORD","Control Flash And Beep","Integer Value: flashAndBeep(2)"]
[40085,"0084","UWORD","Control Turn On UPS Load","Integer Value: upsSmartControlTurnOnUpsLoad(2)"]
[{"$nulls":3},"Test Group"]
[40090,"0089","UWORD","Test Diagnostics","Integer Value: testDiagnostics(2)"]
[]
[]
["Function Code 03 - Read holding Registers."]
[40091,"0090","UWORD","Test Diagnostics Results","Integer Value: ok(1),failed(2),invalidTest(3),testInProgress(4)"]
["                           Three_Phase_UPS"]
[]
[{"$nulls":3},"Battery Group"]
[40100,"0099","UWORD","Battery Voltage","VAC"]
[40101,"0100","UWORD","Battery Capacity","0-100%"]
[40102,"0101","UWORD","Battery Time Remain","Minutes"]
[40103,"0102","UWORD","Battery Current","x0.1 A"]
[40104,null,null,"Battery Temperature","x0.1 ℃"]
[]
[{"$nulls":3},"Input Group"]
[40110,"0109","UWORD","Input Frequency","x0.1 Hz"]
[40111,"0110","UWORD","Input Voltage R","x0.1 VAC"]
[40112,"0111","UWORD","Inpu tVoltage S","x0.1 VAC"]
[40113,"0112","UWORD","Input Voltage T","x0.1 VAC"]
[{"$nulls":3},"Output Group"]
[40120,"0119","UWORD","Output Frequency","x0.1 Hz"]
[40121,"0120","UWORD","Output Voltage R","x0.1 VAC (Output Voltage in the threeInOneOut)"]
[40122,"0121","UWORD","Output Voltage S","x0.1 VAC (equivalent to Register 40124 in the threeInOneOut)"]
[40123,"0122","UWORD","Output Voltage T","x0.1 VAC (equivalent to Register 40101 in the threeInOneOut)"]
[40124,"0123","UWORD","Output Load Percentage R","x0.1 Percentage(Output Load Percentage in the threeInOneOut)"]
[40125,"0124","UWORD","Output Load Percentage S","x0.1 Percentage (No significance in the threeInOneOut)"]
[40126,"0125","UWORD","Output Load Percentage T","x0.1 Percentage (No significance in the threeInOneOut)"]
[{"$nulls":3},"Bypass Group"]
[40130,"0129","UWORD","Bypass Source Frequency","x0.1 Hz"]
[40131,"0130","UWORD","Bypss Source Voltage R","x0.1 VAC"]
[40132,"0131","UWORD","Bypss Source Voltage S","x0.1 VAC"]
[40133,"0132","UWORD","Bypss Source Voltage T","x0.1 VAC"]
[{"$nulls":3},"UPS Status Group"]
[40140,"0139","UWORD","DC and Rectifier Status RecRotError","Integer Value: yes(14),no(16)"]
[40141,"0140","UWORD","DC and Rectifier Status LowBatteryShutdown","Integer Value: yes(14),no(16)"]
[40142,"0141","UWORD","DC and Rectifier Status LowBattery","Integer Value: yes(14),no(16)"]
[40143,"0142","UWORD","DC and Rectifier Status InAndOut","Integer Value: threeInOneOut(2),threeInThreeOut(3)"]
[40144,"0143","UWORD","DC and Rectifier Status BatteryStatus","Integer Value: backup(4),acnormal(5)"]
[40145,"0144","UWORD","DC and Rectifier Status ChargeStatus","Integer Value: boost(6),float(7),no(16)"]
[40146,"0145","UWORD","DC and Rectifier Status RecOperating","Integer Value: yes(14),no(16)"]
[40147,"0146","UWORD","UPS Status Bypass Freqency Fail","Integer Value: yes(14),no(16)"]
[40148,"0147","UWORD","UPS Status Manual Bypass Breaker","Integer Value: close(8),open(9)"]
[40149,"0148","UWORD","UPS Status AC Status","Integer Value: normal(10),abnormal(11)"]
[40150,"0149","UWORD","UPS Status Static Switch Mode","Integer Value: invermode(12),bypassmode(13)"]
[40151,"0150","UWORD","UPS Status Inverter Operating","Integer Value: yes(14),no(16)"]
[{"$nulls":3},"Fault Status Group"]
[40160,"0159","UWORD","Fault Status Emergency Stop","Integer Value: yes(14),no(16)"]
[40161,"0160","UWORD","Fault Status High DC Shutdown","Integer Value: yes(14),no(16)"]
[40162,"0161","UWORD","Fault Status Bypass Breaker","Integer Value: yes(14),no(16)"]
[40163,"0162","UWORD","Fault Status Over Load","Integer Value: yes(14),no(16)"]
[40164,"0163","UWORD","Fault Status Inverter Output Fail","Integer Value: yes(14),no(16)"]
[40165,"0164","UWORD","Fault Status Over Temperature","Integer Value: yes(14),no(16)"]
[40166,"0165","UWORD","Fault Status Short Circuit","Integer Value: yes(14),no(16)"]
[{"$nulls":3},"Rating Group"]
["40170 - 40176","0169 - 0175","14 characters","Rating Rectifier Voltage","14 characters"]
[40177,"0176","UWORD","Rating Rectifier Frequency","Hz"]
["40178 - 40184","0177 - 0183","14 characters","Rating  Source Bypass Voltage","14 characters"]
[40185,"0184","UWORD","Rating Bypass Source Frequency","Hz"]
["40186 - 40192","0185 - 0191","14 characters","Rating Output Voltage","14 characters"]
[40193,"0192","UWORD","Rating Output Frequency","Hz"]
[40194,"0193","UWORD","Rating Battery Voltage","VAC"]
["40195 - 40199","0194 - 0198","10 characters","Rating Power","10 characters"]
["UPS Environment"]
["Function Code 03 - Read holding Registers"]
[{"$nulls":3},"Environment Status"]
[40301,"0300","UWORD","Environment Temperature","x0.1 ℃"]
[40302,"0301","UWORD","Environment Humidity","0-100%"]
[40303,"0302","UWORD","Environment Water","Integer Value: normal(1),abnormal(2)"]
[40304,"0303","UWORD","Environment Gas","Integer Value: normal(1),abnormal(2)"]
[40305,"0304","UWORD","Environment Smoke","Integer Value: normal(1),abnormal(2)"]
[40306,"0305","UWORD","Environment Security1","Integer Value: normal(1),abnormal(2)"]
[40307,"0306","UWORD","Environment Security2","Integer Value: normal(1),abnormal(2)"]
[40308,"0307","UWORD","Environment Security3","Integer Value: normal(1),abnormal(2)"]
[40309,"0308","UWORD","Environment Security4","Integer Value: normal(1),abnormal(2)"]
[40310,"0309","UWORD","Environment Security5","Integer Value: normal(1),abnormal(2)"]
[40311,"0310","UWORD","Environment Security6","Integer Value: normal(1),abnormal(2)"]
[40312,"0311","UWORD","Environment Security7","Integer Value: normal(1),abnormal(2)"]
["Function Code 06 - Write Single Register"]
["Function Code 16 - Write Multiple Registers"]
[{"$nulls":3},"Environment Settings"]
[40401,"0400","UWORD","Environment Over Temperature","x0.1 ℃"]
[40402,"0401","UWORD","Environment Under Temperature","x0.1 ℃"]
[40403,"0402","UWORD","Environment Over Humidity","0-100%"]
[40404,"0403","UWORD","Environment Under Humidity","0-100%"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}